## Highlights
Name | Status | Start date | Created date | Complete date | Last modified date | Completed date | Location | ID | Importance | Status group | Site | Week Start | URL | Updated version | Discipline
0453.ACH04 Chiller Compressor Faulty | In Progress | 2026-06-04 | 2026-06-04 |  | 2026-06-04 |  | DCOE KANBAN system | 4471658030 | Normal | Active | ULA | 2026-06-01 | https://www.wrike.com/open.htm?id=4471658030
2026年6月9日公安部第三研究所开展2026年度等保测评 | In Progress | 2026-06-09 | 2026-06-01 |  | 2026-06-01 |  | DCOE KANBAN system | 4468361324 | Normal | Active | GYA | 2026-06-01 | https://www.wrike.com/open.htm?id=4468361324
[GYA]-Significant Incident Summary-9311.MVST0304 DPR communication failure alarm | In Progress |  | 2026-05-18 |  | 2026-05-18 |  | DCOE KANBAN system | 4459376352 | Normal | Active | GYA | 2026-05-18 | https://www.wrike.com/open.htm?id=4459376352
GYA fire water pipe and compressor not grounding issue | In Progress | 2026-05-14 | 2026-05-14 |  | 2026-05-14 |  | DCOE KANBAN system | 4457578168 | Normal | Active | GYA | 2026-05-11 | https://www.wrike.com/open.htm?id=4457578168
ULA Significant Incident - Leakage in the refrigerant pipeline of 0420.HP.02 System 1 | Completed | 2026-05-08 | 2026-05-14 | 2026-05-28 | 2026-05-28 | 2026-05-28 | DCOE KANBAN system | 4457556296 | Normal | Completed | ULA | 2026-05-11 | https://www.wrike.com/open.htm?id=4457556296
ULA Significant Incident - Municipal Water Supply Low Pressure | Completed | 2026-05-14 | 2026-05-14 | 2026-05-14 | 2026-05-14 | 2026-05-14 | DCOE KANBAN system | 4457555553 | Normal | Completed | ULA | 2026-05-11 | https://www.wrike.com/open.htm?id=4457555553
ULA 4 SCBA pressurized gas cylinders calibration test | Completed | 2026-05-11 | 2026-05-11 | 2026-05-11 | 2026-05-11 | 2026-05-11 | DCOE KANBAN system | 4454607032 | Normal | Completed | ULA | 2026-05-11 | https://www.wrike.com/open.htm?id=4454607032
ULA chilled water bypass filter 0.1um from original 0.22um | Completed | 2026-05-11 | 2026-05-11 | 2026-05-11 | 2026-05-11 | 2026-05-11 | DCOE KANBAN system | 4454606840 | Normal | Completed | ULA | 2026-05-11 | https://www.wrike.com/open.htm?id=4454606840
FOC & SOC screens have color issues along the edges of the screens. | In Progress | 2026-05-11 | 2026-05-11 |  | 2026-05-14 |  | DCOE KANBAN system | 4454603020 | Normal | Active | ULA | 2026-05-11 | https://www.wrike.com/open.htm?id=4454603020
ULA Significant Incident-Water dripping of HPWM pipeline from the 2nd Floor Office Area | Completed | 2026-05-11 | 2026-05-11 | 2026-05-11 | 2026-05-11 | 2026-05-11 | DCOE KANBAN system | 4454602208 | Normal | Completed | ULA | 2026-05-11 | https://www.wrike.com/open.htm?id=4454602208
[GYA]-[P2]- XA.GYA.01.01.4000.06.019.01 PDU phase-B abnormal was captured | Completed | 2026-05-06 | 2026-05-06 | 2026-05-06 | 2026-05-06 | 2026-05-06 | DCOE KANBAN system | 4451949851 | Normal | Completed | GYA | 2026-05-04 | https://www.wrike.com/open.htm?id=4451949851
[GYA]-[P2]- GYA.01.01.5000.04.011.2 PDU phase-B abnormal was captured | Completed | 2026-05-06 | 2026-05-06 | 2026-05-06 | 2026-05-06 | 2026-05-06 | DCOE KANBAN system | 4451941209 | Normal | Completed | GYA | 2026-05-04 | https://www.wrike.com/open.htm?id=4451941209
DH6000 Chiller 1# System 2 high current alarm | Completed | 2026-04-30 | 2026-04-30 | 2026-05-28 | 2026-05-28 | 2026-05-28 | DCOE KANBAN system | 4446770195 | Normal | Completed | ULA | 2026-04-27 | https://www.wrike.com/open.htm?id=4446770195
GYA Data Center - Inspection - Date 20260428 | Completed |  | 2026-04-28 | 2026-04-28 | 2026-04-28 | 2026-04-28 | DCOE KANBAN system | 4444811051 | Normal | Completed | GYA | 2026-04-27 | https://www.wrike.com/open.htm?id=4444811051
[GYA]-Significant Incident Summary-Sprinkler pump-1# in the 0612 room startup unexpectedly | In Progress | 2026-06-04 | 2026-04-25 |  | 2026-06-01 |  | DCOE KANBAN system | 4443412657 | Normal | Active | GYA | 2026-04-20 | https://www.wrike.com/open.htm?id=4443412657
GYA- incident-[P1]-captured the smoke alarm message in the corridor of 0130 area | In Progress | 2026-06-05 | 2026-04-23 |  | 2026-05-28 |  | DCOE KANBAN system | 4441961899 | Normal | Active | GYA | 2026-04-20 | https://www.wrike.com/open.htm?id=4441961899
Diesel oil system PPM bid evaluation | Completed | 2026-04-01 | 2026-04-23 | 2026-05-14 | 2026-05-14 | 2026-05-14 | DCOE KANBAN system | 4441665836 | Normal | Completed | ULA | 2026-04-20 | https://www.wrike.com/open.htm?id=4441665836
Chahar Park Branch of the Market Supervision Administration and Special Equipment Inspection Institute visit ULA site | Completed | 2026-04-23 | 2026-04-23 | 2026-04-23 | 2026-04-23 | 2026-04-23 | DCOE KANBAN system | 4441654170 | Normal | Completed | ULA | 2026-04-20 | https://www.wrike.com/open.htm?id=4441654170
Massive alarm in EPMS | Completed | 2026-04-23 | 2026-04-23 | 2026-04-23 | 2026-04-23 | 2026-04-23 | DCOE KANBAN system | 4441652392 | Normal | Completed | ULA | 2026-04-20 | https://www.wrike.com/open.htm?id=4441652392
PSG 5003 server display screen no response | Completed | 2026-04-23 | 2026-04-23 | 2026-04-23 | 2026-04-23 | 2026-04-23 | DCOE KANBAN system | 4441651643 | Normal | Completed | ULA | 2026-04-20 | https://www.wrike.com/open.htm?id=4441651643
ULA Significant Incident - PSG 5003 Server Unresponsive | Completed | 2026-04-23 | 2026-04-23 | 2026-04-23 | 2026-04-23 | 2026-04-23 | DCOE KANBAN system | 4441639840 | Normal | Completed | ULA | 2026-04-20 | https://www.wrike.com/open.htm?id=4441639840
GYA conducted emergency fire evacuation drill on Apr. 22 | Completed | 2026-04-22 | 2026-04-22 | 2026-04-22 | 2026-04-23 | 2026-04-22 | DCOE KANBAN system | 4440969532 | Normal | Completed | GYA | 2026-04-20 | https://www.wrike.com/open.htm?id=4440969532
Fire Safety Inspection -Apr. 21 | Completed | 2026-04-21 | 2026-04-22 | 2026-04-22 | 2026-04-22 | 2026-04-22 | DCOE KANBAN system | 4440698332 | Normal | Completed | GYA | 2026-04-20 | https://www.wrike.com/open.htm?id=4440698332
Weekend CME work order | Completed | 2026-04-20 | 2026-04-20 | 2026-04-23 | 2026-04-23 | 2026-04-23 | DCOE KANBAN system | 4438784995 | Normal | Completed | ULA | 2026-04-20 | https://www.wrike.com/open.htm?id=4438784995
0447-1# Chiller system 2 faulty, Faulty code 54 | Completed | 2026-04-20 | 2026-04-20 | 2026-04-23 | 2026-04-23 | 2026-04-23 | DCOE KANBAN system | 4438783935 | Normal | Completed | ULA | 2026-04-20 | https://www.wrike.com/open.htm?id=4438783935
0443 Pump Skid 3#VFD and Outdoor Air Hanging Plate Test Report | Completed | 2026-04-16 | 2026-04-16 | 2026-05-14 | 2026-05-14 | 2026-05-14 | DCOE KANBAN system | 4436710055 | Normal | Completed | ULA | 2026-04-13 | https://www.wrike.com/open.htm?id=4436710055
0447-3# Cold Machine System 2 fault, Code 33 (Oil separator ejector fault) | Completed | 2026-04-16 | 2026-04-16 | 2026-05-14 | 2026-05-14 | 2026-05-14 | DCOE KANBAN system | 4436706768 | Normal | Completed | ULA | 2026-04-13 | https://www.wrike.com/open.htm?id=4436706768
[GYA]-Significant Incident Summary-5304 PLCA failure alarm | In Progress | 2026-04-12 | 2026-04-13 |  | 2026-06-01 |  | DCOE KANBAN system | 4433821968 | Normal | Active | GYA | 2026-04-13 | https://www.wrike.com/open.htm?id=4433821968
Domestic water pressure low | Completed | 2026-04-13 | 2026-04-13 | 2026-04-13 | 2026-04-13 | 2026-04-13 | DCOE KANBAN system | 4433768164 | Normal | Completed | ULA | 2026-04-13 | https://www.wrike.com/open.htm?id=4433768164
4601 HPWM compressed air pipe leak | Completed | 2026-05-29 | 2026-04-13 | 2026-05-28 | 2026-05-28 | 2026-05-28 | DCOE KANBAN system | 4433766819 | Normal | Completed | ULA | 2026-04-13 | https://www.wrike.com/open.htm?id=4433766819
The low-voltage switchgear in Room 5304 is vibrating and making a loud noise. | Completed | 2026-04-09 | 2026-04-09 | 2026-05-28 | 2026-05-28 | 2026-05-28 | DCOE KANBAN system | 4431434212 | Normal | Completed | ULA | 2026-04-06 | https://www.wrike.com/open.htm?id=4431434212
Phase B indicator light of XA.ULA.01.01.6000.10.020 PDU1 is off | Completed | 2026-04-09 | 2026-04-09 | 2026-04-09 | 2026-04-09 | 2026-04-09 | DCOE KANBAN system | 4431428886 | Normal | Completed | ULA | 2026-04-06 | https://www.wrike.com/open.htm?id=4431428886
Self-inspection form Filling for online energy Monitoring of key energy-consuming enterprise in Ulanqab City | Completed | 2026-04-09 | 2026-04-09 | 2026-04-09 | 2026-04-09 | 2026-04-09 | DCOE KANBAN system | 4431425737 | Normal | Completed | ULA | 2026-04-06 | https://www.wrike.com/open.htm?id=4431425737
ULA HPWM system fore jockey pump 2 surge tanks and 1 check valve, 5 gaskets procurement request | Completed | 2026-04-09 | 2026-04-09 | 2026-04-09 | 2026-04-09 | 2026-04-09 | DCOE KANBAN system | 4431420424 | Normal | Completed | ULA | 2026-04-06 | https://www.wrike.com/open.htm?id=4431420424
ULA leaked HPWM system fire jockey pump surge tank repair procurement request | Completed | 2026-04-09 | 2026-04-09 | 2026-04-09 | 2026-04-09 | 2026-04-09 | DCOE KANBAN system | 4431418828 | Normal | Completed | ULA | 2026-04-06 | https://www.wrike.com/open.htm?id=4431418828
[GYA]-Significant Incident Summary -0447.ACH02 sys2 high motor temperature alarm | Completed | 2026-04-08 | 2026-04-09 | 2026-04-22 | 2026-04-22 | 2026-04-22 | DCOE KANBAN system | 4431417915 | Normal | Completed | GYA | 2026-04-06 | https://www.wrike.com/open.htm?id=4431417915
[GYA]-Significant Incident Summary-0503.ASD01C 24V power panel failure | Completed |  | 2026-04-07 | 2026-04-07 | 2026-04-07 | 2026-04-07 | DCOE KANBAN system | 4429450308 | Normal | Completed | GYA | 2026-04-06 | https://www.wrike.com/open.htm?id=4429450308
GYA site additional Diesel Fuel Sampling and Testing Services purchase application | In Progress | 2026-04-03 | 2026-04-03 |  | 2026-04-22 |  | DCOE KANBAN system | 4428015935 | Normal | Active | GYA | 2026-03-30 | https://www.wrike.com/open.htm?id=4428015935
Emergency Purchase- GYA site Fire Alarm Control Panel OEM Technical Support Service and spare parts purchase request | Completed |  | 2026-04-03 | 2026-04-03 | 2026-04-03 | 2026-04-03 | DCOE KANBAN system | 4427990093 | Normal | Completed | GYA | 2026-03-30 | https://www.wrike.com/open.htm?id=4427990093
GYA&ULA digital industrial supply platform service purchase application | In Progress | 2026-04-03 | 2026-04-03 |  | 2026-04-22 |  | DCOE KANBAN system | 4427989507 | Normal | Active | GYA | 2026-03-30 | https://www.wrike.com/open.htm?id=4427989507
GYA out-of-warranty repair service basic and exceeded labor-hour for 2025/12/4-2026/3/3 (3-month) | Completed |  | 2026-04-03 | 2026-04-03 | 2026-04-03 | 2026-04-03 | DCOE KANBAN system | 4427987981 | Normal | Completed | GYA | 2026-03-30 | https://www.wrike.com/open.htm?id=4427987981
GYA a new iMac Pro 2017 purchase application | In Progress | 2026-04-03 | 2026-04-03 |  | 2026-04-22 |  | DCOE KANBAN system | 4427987848 | Normal | Active | GYA | 2026-03-30 | https://www.wrike.com/open.htm?id=4427987848
ULA Data Building Domestic Water Pipes Do Not Form a Closed Ring | In Progress | 2026-04-02 | 2026-04-02 |  | 2026-04-20 |  | DCOE KANBAN system | 4426656540 | Normal | Active | ULA | 2026-03-30 | https://www.wrike.com/open.htm?id=4426656540
ULA P2 Incident- The connector of pressure stabilizing pump in water mist system in 5601 leakage. | Completed | 2026-04-02 | 2026-04-02 | 2026-05-28 | 2026-05-28 | 2026-05-28 | DCOE KANBAN system | 4426645938 | Normal | Completed | ULA | 2026-03-30 | https://www.wrike.com/open.htm?id=4426645938
Spare parts procurement request for ULA VC LED wall pink issue repair | Completed | 2026-04-02 | 2026-04-02 | 2026-04-02 | 2026-04-02 | 2026-04-02 | DCOE KANBAN system | 4426632357 | Normal | Completed | ULA | 2026-03-30 | https://www.wrike.com/open.htm?id=4426632357
Exception approval for ULA 4 break fix works | Completed | 2026-04-02 | 2026-04-02 | 2026-04-02 | 2026-04-02 | 2026-04-02 | DCOE KANBAN system | 4426629808 | Normal | Completed | ULA | 2026-03-30 | https://www.wrike.com/open.htm?id=4426629808
Chemical cleaning service for 0447-1 chiller condenser fins as FOK | Completed | 2026-04-02 | 2026-04-02 | 2026-04-02 | 2026-04-02 | 2026-04-02 | DCOE KANBAN system | 4426628672 | Normal | Completed | ULA | 2026-03-30 | https://www.wrike.com/open.htm?id=4426628672
ULA out-of-warranty service basic fixed labor-hour and exceeded labor-hour for Q4 (2025/12/18-2026/3/17) | Completed | 2026-04-02 | 2026-04-02 | 2026-04-02 | 2026-04-02 | 2026-04-02 | DCOE KANBAN system | 4426626915 | Normal | Completed | ULA | 2026-03-30 | https://www.wrike.com/open.htm?id=4426626915
[GYA]- incident P1-1# Fire host failure with its display screen malfunction | Completed | 2026-03-27 | 2026-03-29 | 2026-03-29 | 2026-03-29 | 2026-03-29 | DCOE KANBAN system | 4420699430 | Normal | Completed | GYA | 2026-03-23 | https://www.wrike.com/open.htm?id=4420699430
[GYA]-Significant Incident Summary -0443.ACH03 sys2 fan fault alarm | Completed | 2026-03-25 | 2026-03-25 | 2026-04-01 | 2026-04-01 | 2026-04-01 | DCOE KANBAN system | 4416014754 | Normal | Completed | GYA | 2026-03-23 | https://www.wrike.com/open.htm?id=4416014754
ULA DH3000 1#chiller system-2 cooling fan replacement service procurement request | Completed | 2026-03-25 | 2026-03-25 | 2026-03-26 | 2026-03-26 | 2026-03-26 | DCOE KANBAN system | 4415805749 | Normal | Completed | ULA | 2026-03-23 | https://www.wrike.com/open.htm?id=4415805749
GYA drill- 9302.Gen08 urea dosing box leakage | Completed | 2026-03-23 | 2026-03-23 | 2026-03-23 | 2026-03-23 | 2026-03-23 | DCOE KANBAN system | 4413175654 | Normal | Completed | GYA | 2026-03-23 | https://www.wrike.com/open.htm?id=4413175654
ULA Significant Incident - Utility Source B Power Sag | Completed | 2026-03-23 | 2026-03-23 | 2026-03-23 | 2026-03-23 | 2026-03-23 | DCOE KANBAN system | 4413174781 | Normal | Completed | ULA | 2026-03-23 | https://www.wrike.com/open.htm?id=4413174781
GYA air duct bracket issue | In Progress | 2026-03-13 | 2026-03-19 |  | 2026-03-19 |  | DCOE KANBAN system | 4410027474 | Normal | Active | GYA | 2026-03-16 | https://www.wrike.com/open.htm?id=4410027474
XA.ULA.01.01.6000.09.005.2 Loss of Phase B | Completed | 2026-03-19 | 2026-03-19 | 2026-03-19 | 2026-03-19 | 2026-03-19 | DCOE KANBAN system | 4409833998 | Normal | Completed | ULA | 2026-03-16 | https://www.wrike.com/open.htm?id=4409833998
Municipal Water Supply Low Pressure | Completed | 2026-03-19 | 2026-03-19 | 2026-03-19 | 2026-03-19 | 2026-03-19 | DCOE KANBAN system | 4409833673 | Normal | Completed | ULA | 2026-03-16 | https://www.wrike.com/open.htm?id=4409833673
GYA PSB plan to add 10Kv MV cable in front of DC | Completed | 2026-03-18 | 2026-03-18 | 2026-05-18 | 2026-05-18 | 2026-05-18 | DCOE KANBAN system | 4408733349 | Normal | Completed | GYA | 2026-03-16 | https://www.wrike.com/open.htm?id=4408733349
GYA 2025 Annual Fire Inspection Result and C-Class Non-Conformity Report | Completed | 2026-03-18 | 2026-03-18 | 2026-03-18 | 2026-03-19 | 2026-03-18 | DCOE KANBAN system | 4408715556 | Normal | Completed | GYA | 2026-03-16 | https://www.wrike.com/open.htm?id=4408715556
[GYA]-significant Incident Summary- 0301 electrical equipments communication failure alarm on EPMS | Completed | 2026-03-15 | 2026-03-16 | 2026-03-16 | 2026-03-16 | 2026-03-16 | DCOE KANBAN system | 4406620259 | Normal | Completed | GYA | 2026-03-16 | https://www.wrike.com/open.htm?id=4406620259
The Water Meter in the Underground Pump Room for Municipal Water Supply Shows an Abnormally High Water Consumption | Completed | 2026-03-16 | 2026-03-16 | 2026-06-05 | 2026-06-05 | 2026-06-05 | DCOE KANBAN system | 4406613191 | Normal | Completed | ULA | 2026-03-16 | https://www.wrike.com/open.htm?id=4406613191
Purified Water Dosing Procedure for Urea Solution | Completed | 2026-03-12 | 2026-03-12 | 2026-04-20 | 2026-04-20 | 2026-04-20 | DCOE KANBAN system | 4402303019 | Normal | Completed | ULA | 2026-03-09 | https://www.wrike.com/open.htm?id=4402303019
GEN 12# Engine Control Not In Auto | Completed | 2026-03-10 | 2026-03-12 | 2026-03-12 | 2026-03-12 | 2026-03-12 | DCOE KANBAN system | 4402300501 | Normal | Completed | ULA | 2026-03-09 | https://www.wrike.com/open.htm?id=4402300501
GEN 24# Engine Control Not In Auto | Completed | 2026-03-12 | 2026-03-12 | 2026-03-12 | 2026-03-12 | 2026-03-12 | DCOE KANBAN system | 4402299582 | Normal | Completed | ULA | 2026-03-09 | https://www.wrike.com/open.htm?id=4402299582
0441.ACH04 Outlet Valve Failure Alarm | Completed | 2026-03-09 | 2026-03-09 | 2026-03-09 | 2026-03-09 | 2026-03-09 | DCOE KANBAN system | 4392331155 | Normal | Completed | ULA | 2026-03-09 | https://www.wrike.com/open.htm?id=4392331155
[GYA]-Significant Incident-IT team captured potential server-level high temperature alarm in Room 0505 | Completed | 2026-03-06 | 2026-03-07 | 2026-03-07 | 2026-03-07 | 2026-03-07 | DCOE KANBAN system | 4392048597 | Normal | Completed | GYA | 2026-03-02 | https://www.wrike.com/open.htm?id=4392048597
GYA external visit on Mar. 9 | Completed | 2026-03-09 | 2026-03-06 | 2026-03-12 | 2026-03-12 | 2026-03-12 | DCOE KANBAN system | 4391339148 | Normal | Completed | GYA | 2026-03-02 | https://www.wrike.com/open.htm?id=4391339148
GYA Vending machine potential risk | Completed | 2026-03-06 | 2026-03-06 | 2026-03-06 | 2026-03-06 | 2026-03-06 | DCOE KANBAN system | 4391338464 | Normal | Completed | GYA | 2026-03-02 | https://www.wrike.com/open.htm?id=4391338464
City water consumption plan | Completed | 2026-03-05 | 2026-03-05 | 2026-03-05 | 2026-03-05 | 2026-03-05 | DCOE KANBAN system | 4390163188 | Normal | Completed | ULA | 2026-03-02 | https://www.wrike.com/open.htm?id=4390163188
ULA HSE Room Total Cooling Loss Incident | Completed | 2026-03-02 | 2026-03-02 | 2026-04-14 | 2026-04-14 | 2026-04-14 | DCOE KANBAN system | 4386836039 | Normal | Completed | ULA | 2026-03-02 | https://www.wrike.com/open.htm?id=4386836039
GYA PAV quick exhaust valve issue | Completed |  | 2026-03-02 | 2026-03-02 | 2026-03-02 | 2026-03-02 | DCOE KANBAN system | 4386835285 | Normal | Completed | GYA | 2026-03-02 | https://www.wrike.com/open.htm?id=4386835285
0462 Fuel polishers leakage | Completed | 2026-02-26 | 2026-02-26 | 2026-04-02 | 2026-04-02 | 2026-04-02 | DCOE KANBAN system | 4384784078 | Normal | Completed | ULA | 2026-02-23 | https://www.wrike.com/open.htm?id=4384784078
Combustable air detectors replacement suggestion | Completed | 2026-02-25 | 2026-02-25 | 2026-06-05 | 2026-06-05 | 2026-06-05 | DCOE KANBAN system | 4383787638 | Normal | Completed | ULA | 2026-02-23 | https://www.wrike.com/open.htm?id=4383787638
Proaction valve pressure higher than the normal range on the air system side | Completed | 2026-02-25 | 2026-02-25 | 2026-05-28 | 2026-05-28 | 2026-05-28 | DCOE KANBAN system | 4383786532 | Normal | Completed | ULA | 2026-02-23 | https://www.wrike.com/open.htm?id=4383786532
GEN08 return fuel pipe leakage | Completed | 2026-02-27 | 2026-02-25 | 2026-05-14 | 2026-05-14 | 2026-05-14 | DCOE KANBAN system | 4383784881 | Normal | Completed | ULA | 2026-02-23 | https://www.wrike.com/open.htm?id=4383784881
Suspected 9320.GEN21 Lube Oil Leakage | Completed | 2026-02-25 | 2026-02-25 | 2026-02-26 | 2026-02-26 | 2026-02-26 | DCOE KANBAN system | 4383784587 | Normal | Completed | ULA | 2026-02-23 | https://www.wrike.com/open.htm?id=4383784587
0443.ACH01 Fan Fault on System 2 | Completed | 2026-02-25 | 2026-02-25 | 2026-05-28 | 2026-05-28 | 2026-05-28 | DCOE KANBAN system | 4383784244 | Normal | Completed | ULA | 2026-02-23 | https://www.wrike.com/open.htm?id=4383784244
Replace colorchip in 0506 | Completed | 2026-02-25 | 2026-02-25 | 2026-02-26 | 2026-02-26 | 2026-02-26 | DCOE KANBAN system | 4383780882 | Normal | Completed | ULA | 2026-02-23 | https://www.wrike.com/open.htm?id=4383780882
[GYA]-Significant Incident-High motor current alarm in 0443.ACH04 SYS1 | Completed | 2026-02-15 | 2026-02-16 | 2026-02-16 | 2026-02-16 | 2026-02-16 | DCOE KANBAN system | 4375511216 | Normal | Completed | GYA | 2026-02-16 | https://www.wrike.com/open.htm?id=4375511216
Ulanqab TeleCommunications Administration Office Visit ULA site on 9th-Feb | Completed | 2026-02-12 | 2026-02-11 | 2026-02-12 | 2026-02-12 | 2026-02-12 | DCOE KANBAN system | 4373119740 | Normal | Completed | ULA | 2026-02-09 | https://www.wrike.com/open.htm?id=4373119740
Special Equipment Institute Plan to ULA site for safety check before spring festival | Completed | 2026-02-12 | 2026-02-11 | 2026-02-12 | 2026-02-12 | 2026-02-12 | DCOE KANBAN system | 4373118615 | Normal | Completed | ULA | 2026-02-09 | https://www.wrike.com/open.htm?id=4373118615
Road surface cracking and subsidence in north oil tank area | Completed | 2026-02-12 | 2026-02-11 | 2026-03-09 | 2026-03-09 | 2026-03-09 | DCOE KANBAN system | 4373114810 | Normal | Completed | ULA | 2026-02-09 | https://www.wrike.com/open.htm?id=4373114810
GYA elevator issue | Completed | 2026-02-09 | 2026-02-09 | 2026-02-09 | 2026-02-09 | 2026-02-09 | DCOE KANBAN system | 4370118109 | Normal | Completed | GYA | 2026-02-09 | https://www.wrike.com/open.htm?id=4370118109
ULA Significant Incident -Water dripping of HPWM pipeline in 9110 corridor in Generator building | Completed | 2026-02-09 | 2026-02-09 | 2026-02-11 | 2026-02-11 | 2026-02-11 | DCOE KANBAN system | 4370117423 | Normal | Completed | ULA | 2026-02-09 | https://www.wrike.com/open.htm?id=4370117423
[Drill]-GYA-P2-EPMS primary server failure | Completed | 2026-02-06 | 2026-02-06 | 2026-02-06 | 2026-02-06 | 2026-02-06 | DCOE KANBAN system | 4368613855 | Normal | Completed | GYA | 2026-02-02 | https://www.wrike.com/open.htm?id=4368613855
GYA DC Safety Inspection From GCBD Group | Completed | 2026-02-05 | 2026-02-03 | 2026-02-06 | 2026-02-06 | 2026-02-06 | DCOE KANBAN system | 4364994703 | Normal | Completed | GYA | 2026-02-02 | https://www.wrike.com/open.htm?id=4364994703
Sealant filling for profiled steel plate gaps | Completed | 2026-02-02 | 2026-02-02 | 2026-04-20 | 2026-04-20 | 2026-04-20 | DCOE KANBAN system | 4363819451 | Normal | Completed | ULA | 2026-02-02 | https://www.wrike.com/open.htm?id=4363819451
4601 Pre action valve water flow noise | Completed | 2026-02-02 | 2026-02-02 | 2026-02-11 | 2026-02-11 | 2026-02-11 | DCOE KANBAN system | 4363818435 | Normal | Completed | ULA | 2026-02-02 | https://www.wrike.com/open.htm?id=4363818435
ULA plan to remove the door of printer room | Completed | 2026-02-02 | 2026-02-02 | 2026-02-11 | 2026-02-11 | 2026-02-11 | DCOE KANBAN system | 4363812744 | Normal | Completed | ULA | 2026-02-02 | https://www.wrike.com/open.htm?id=4363812744
ULA Significant Incident - 0929 Office Area was leaked from the water purifier drain in the second-floor tea room. | Completed | 2026-02-02 | 2026-02-02 | 2026-02-11 | 2026-02-11 | 2026-02-11 | DCOE KANBAN system | 4363811103 | Normal | Completed | ULA | 2026-02-02 | https://www.wrike.com/open.htm?id=4363811103
ULA Significant Incident - 6301.UPS05 Critical Alarm | Completed | 2026-02-02 | 2026-02-02 | 2026-02-11 | 2026-02-11 | 2026-02-11 | DCOE KANBAN system | 4363810680 | Normal | Completed | ULA | 2026-02-02 | https://www.wrike.com/open.htm?id=4363810680
Access Room 0506 for the Fire cable L3 test in Zone F | Completed | 2026-02-02 | 2026-02-02 | 2026-02-11 | 2026-02-11 | 2026-02-11 | DCOE KANBAN system | 4363810424 | Normal | Completed | ULA | 2026-02-02 | https://www.wrike.com/open.htm?id=4363810424
GYA gateway firmware upgrade communication | Not Started |  | 2026-01-30 |  | 2026-02-05 |  | DCOE KANBAN system | 4362706911 | Normal | Active | GYA | 2026-01-26 | https://www.wrike.com/open.htm?id=4362706911
GYA Drill- P1-Dual Utility Power Lost on MVSTs on Jan. 30th | Completed | 2026-01-30 | 2026-01-30 | 2026-01-30 | 2026-01-30 | 2026-01-30 | DCOE KANBAN system | 4362606501 | Normal | Completed | GYA | 2026-01-26 | https://www.wrike.com/open.htm?id=4362606501
Pure water test results | Completed | 2026-01-26 | 2026-01-26 | 2026-01-26 | 2026-01-26 | 2026-01-26 | DCOE KANBAN system | 4357482993 | Normal | Completed | ULA | 2026-01-26 | https://www.wrike.com/open.htm?id=4357482993
ULA Significant Incident - Dry-type Fire Sprinkler Leakage in the Q & R Areas of Generators Building | Completed | 2026-01-26 | 2026-01-26 | 2026-02-11 | 2026-02-11 | 2026-02-11 | DCOE KANBAN system | 4357480390 | Normal | Completed | ULA | 2026-01-26 | https://www.wrike.com/open.htm?id=4357480390
ULA Significant Incident - Municipal Water Supply Low Pressure | Completed | 2026-01-26 | 2026-01-26 | 2026-01-26 | 2026-01-26 | 2026-01-26 | DCOE KANBAN system | 4357480134 | Normal | Completed | ULA | 2026-01-26 | https://www.wrike.com/open.htm?id=4357480134
Procurement request - HPWM pump safety relief valve, fire system wall installed PA speaker for ULA site | Completed | 2026-01-22 | 2026-01-22 | 2026-01-22 | 2026-01-22 | 2026-01-22 | DCOE KANBAN system | 4354866071 | Normal | Completed | ULA | 2026-01-19 | https://www.wrike.com/open.htm?id=4354866071
Fire modeler rectify in 0506 | Completed | 2026-01-22 | 2026-01-22 | 2026-02-11 | 2026-02-11 | 2026-02-11 | DCOE KANBAN system | 4354857462 | Normal | Completed | ULA | 2026-01-19 | https://www.wrike.com/open.htm?id=4354857462
开放办公区吊顶内未配置烟感探测器沟通事宜 | Completed | 2026-01-19 | 2026-01-21 | 2026-01-26 | 2026-01-26 | 2026-01-26 | DCOE KANBAN system | 4353937931 | Normal | Completed | GYA | 2026-01-19 | https://www.wrike.com/open.htm?id=4353937931
数据中心消防安全责任人变更 | Completed | 2026-01-20 | 2026-01-20 | 2026-02-04 | 2026-02-04 | 2026-02-04 | DCOE KANBAN system | 4352888787 | Normal | Completed | GYA | 2026-01-19 | https://www.wrike.com/open.htm?id=4352888787
Urea solution dilution test | Completed | 2026-01-19 | 2026-01-19 | 2026-01-22 | 2026-01-22 | 2026-01-22 | DCOE KANBAN system | 4351944958 | Normal | Completed | ULA | 2026-01-19 | https://www.wrike.com/open.htm?id=4351944958
ULA Significant Incident - Municipal Water Supply Low Pressure | Completed | 2026-01-19 | 2026-01-19 | 2026-01-22 | 2026-01-22 | 2026-01-22 | DCOE KANBAN system | 4351944201 | Normal | Completed | ULA | 2026-01-19 | https://www.wrike.com/open.htm?id=4351944201
[GYA]-Significant Incident Summary-Utility Source B Power Sag | Completed |  | 2026-01-16 | 2026-01-16 | 2026-01-16 | 2026-01-16 | DCOE KANBAN system | 4350782980 | Normal | Completed | GYA | 2026-01-12 | https://www.wrike.com/open.htm?id=4350782980
ULA Significant Incident - water dripping in DH6000 N1 corridor area and loading dock area, no impact to equipment and DH | Completed | 2026-01-15 | 2026-01-14 | 2026-01-15 | 2026-01-15 | 2026-01-15 | DCOE KANBAN system | 4349768452 | Normal | Completed | ULA | 2026-01-12 | https://www.wrike.com/open.htm?id=4349768452
ULA Significant Incident - 0457. ACH04 Fault Shutdown Warning | Completed | 2026-01-15 | 2026-01-14 | 2026-01-15 | 2026-01-15 | 2026-01-15 | DCOE KANBAN system | 4349767853 | Normal | Completed | ULA | 2026-01-12 | https://www.wrike.com/open.htm?id=4349767853
[GYA]-Significant Incident Summary-Utility Source A Power Sag | Completed | 2026-01-08 | 2026-01-09 | 2026-01-09 | 2026-01-09 | 2026-01-09 | DCOE KANBAN system | 4345580002 | Normal | Completed | GYA | 2026-01-05 | https://www.wrike.com/open.htm?id=4345580002
Change optical module 0506 | Completed | 2026-01-06 | 2026-01-08 | 2026-01-08 | 2026-01-08 | 2026-01-08 | DCOE KANBAN system | 4344498023 | Normal | Completed | ULA | 2026-01-05 | https://www.wrike.com/open.htm?id=4344498023
GYA- camera installation proposal in elevator | Completed | 2026-01-08 | 2026-01-08 | 2026-06-01 | 2026-06-01 | 2026-06-01 | DCOE KANBAN system | 4344493076 | Normal | Completed | GYA | 2026-01-05 | https://www.wrike.com/open.htm?id=4344493076
ULA P1 Incident - Generator 17# and 25# not in automatic position | Completed | 2026-01-05 | 2026-01-08 | 2026-01-08 | 2026-01-08 | 2026-01-08 | DCOE KANBAN system | 4344490937 | Normal | Completed | ULA | 2026-01-05 | https://www.wrike.com/open.htm?id=4344490937
ULA maintenance spare parts and tool request | Completed | 2026-01-08 | 2026-01-08 | 2026-01-08 | 2026-01-08 | 2026-01-08 | DCOE KANBAN system | 4344489431 | Normal | Completed | ULA | 2026-01-05 | https://www.wrike.com/open.htm?id=4344489431
Fire and Rescue Brigade of Ulanqab Visit ULA Site | Completed | 2026-01-07 | 2026-01-08 | 2026-01-08 | 2026-01-08 | 2026-01-08 | DCOE KANBAN system | 4344488483 | Normal | Completed | ULA | 2026-01-05 | https://www.wrike.com/open.htm?id=4344488483
GYA 220KV Linka transformer 2# maintenance notification | Completed | 2026-01-08 | 2026-01-07 | 2026-01-12 | 2026-01-12 | 2026-01-12 | DCOE KANBAN system | 4343515153 | Normal | Completed | GYA | 2026-01-05 | https://www.wrike.com/open.htm?id=4343515153
ULA Significant Incident - Municipal Water Supply Low Pressure | Completed | 2026-01-05 | 2026-01-05 | 2026-01-05 | 2026-01-05 | 2026-01-05 | DCOE KANBAN system | 4341416438 | Normal | Completed | ULA | 2026-01-05 | https://www.wrike.com/open.htm?id=4341416438
AIPO New MECH Engineer Onboard | Completed | 2026-01-05 | 2026-01-05 | 2026-01-05 | 2026-01-05 | 2026-01-05 | DCOE KANBAN system | 4341415632 | Normal | Completed | ULA | 2026-01-05 | https://www.wrike.com/open.htm?id=4341415632
New Year Thanks Letter Form WLCB Big Data Bureau | Completed | 2026-01-05 | 2026-01-05 | 2026-01-05 | 2026-01-05 | 2026-01-05 | DCOE KANBAN system | 4341414982 | Normal | Completed | ULA | 2026-01-05 | https://www.wrike.com/open.htm?id=4341414982
GYA 4601 high pressure water mist system pump set relief valve internal leakage | In Progress | 2025-12-31 | 2026-01-03 |  | 2026-01-28 |  | DCOE KANBAN system | 4341248869 | Normal | Active | GYA | 2025-12-29 | https://www.wrike.com/open.htm?id=4341248869
[R3]-[June-8-2026]-[ULA]-[Electrical]-[Preventive Maintenance] -Perform PH1/2/3 diesel generator sets &SCR Annual PPM. | Closed | 2026-06-08 09:00:00 | 2026-06-01 10:58:42 |  |  | 2026-06-21 21:00:00 | CR | CHG0035987 |  | Completed | ULA | 2026-06-01 | https://aipostation.apzones.com/change_request.do?sys_id=02bfce00975d0f907d637606c853afe0&sysparm_record_target=change_request&sysparm_record_row=7&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Status updated from In Progress to Closed, URL updated
[R3]-[6/15/2026]-[GYA]-[BMS]-[Preventive maintenance]-Annually calibration on chilled water pipeline(Flow meter / temperature sensor) | Implement | 2026-06-15 09:30:00 | 2026-06-08 08:38:27 |  |  | 2026-06-26 20:00:00 | CR | CHG0036020 |  | Active | GYA | 2026-06-08 | https://aipostation.apzones.com/change_request.do?sys_id=08c231de971d83107d637606c853af6e&sysparm_record_target=change_request&sysparm_record_row=3&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Status updated from In Progress to Implement; [2026-06-23] URL updated; [2026-06-23] URL updated
[R3] -[06/11/2026]-[GYA] -[Mechanical] -[Preventive Maintenance] - Quarterly Day Tank Diesel Oil Recirculation | Closed | 2026-06-11 09:00:00 | 2026-06-04 11:06:03 |  |  | 2026-06-25 18:00:00 | CR | CHG0036005 |  | Completed | GYA | 2026-06-01 | https://aipostation.apzones.com/change_request.do?sys_id=0b2ea985979583d07d637606c853af19&sysparm_record_target=change_request&sysparm_record_row=5&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Status updated from In Progress to Closed, URL updated
[R3]-[Jun-09-2026]-[ULA]-[Mechanical]-[Preventive Maintenance] - Chiller Semi Annual PPM& Annual PPM | Closed | 2026-06-09 09:00:00 | 2026-06-04 11:21:14 |  |  | 2026-06-21 22:22:38 | CR | CHG0036006 |  | Completed | ULA | 2026-06-01 | https://aipostation.apzones.com/change_request.do?sys_id=11a1fdc59799c3d064f17606c853af59&sysparm_record_target=change_request&sysparm_record_row=8&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Status updated from In Progress to Closed, URL updated
[R3] -[Jun-01-2026]-[ULA]-[BMS]-[Preventive Maintenance]- BMS two Monthly Preventive Maintenance | In Progress | 2026-06-01 | 2026-05-27 |  |  |  | CR | CHG0035954 |  | Active | ULA | 2026-05-25 | https://aipostation.apzones.com/change_request.do?sys_id=2433dcee97c9c39064f17606c853afdc&sysparm_record_target=change_request&sysparm_record_row=5&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id
[R2]-[22nd-Jun-2026]-[GYA]-[CFM]-[Electrical]-[Preventive Maintenance] - stage 3-Phase I&II&III UPS Annual PPM | Implement | 2026-06-22 09:00:00 | 2026-05-15 13:53:53 |  |  | 2026-07-05 18:00:00 | CR | CHG0035917 |  | Active | GYA | 2026-05-11 | https://aipostation.apzones.com/change_request.do?sys_id=26c45bae97f04f107d637606c853afda&sysparm_record_target=change_request&sysparm_record_row=18&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Status updated from In Progress to Implement; [2026-06-23] URL updated
[R1]-[June-16-2026]-[ULA]-[Fire]-[improvement]GGBM25 #3.8 3601 high pressure water mist tank replacement | Authorize | 2026-06-16 | 2026-06-05 |  |  |  | CR | CHG0036018 |  | Active | ULA | 2026-06-01 | https://aipostation.apzones.com/change_request.do?sys_id=28a5c8a9975187d064f17606c853af95&sysparm_record_target=change_request&sysparm_record_row=7&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Status updated from In Progress to Authorize
[R3]-[Jun-03-2026]-[ULA]-[Mechanical]-[Preventive Maintenance] - Pump Skid Semi Annual PPM& Annual PPM | In Progress | 2026-06-03 | 2026-05-29 |  |  |  | CR | CHG0035980 |  | Active | ULA | 2026-05-25 | https://aipostation.apzones.com/change_request.do?sys_id=2e31628b97890b907d637606c853aff6&sysparm_record_target=change_request&sysparm_record_row=8&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id
[R2] -[May-20-2026]-[ULA] - [Fire Service]- [Preventive Maintenance] - Fire single point test of Zone C/D（3000.4000） | New | 2026-05-20 | 2026-05-05 |  |  |  | CR | CHG0035859 |  | Active | ULA | 2026-05-04 | https://aipostation.apzones.com/change_request.do?sys_id=3365a1af97e803d064f17ac8d853afa2&sysparm_record_target=change_request&sysparm_record_row=9&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Status updated from In Progress to New
[R3]-[6/1/2026]-[GYA]-[BMS]-[Preventive maintenance]-Bi-Monthly BMS maintenance | In Progress | 2026-06-01 | 2026-05-26 |  |  |  | CR | CHG0035952 |  | Active | GYA | 2026-05-25 | https://aipostation.apzones.com/change_request.do?sys_id=368587069745c3907d637606c853afb7&sysparm_record_target=change_request&sysparm_record_row=10&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id
[R3]-[GYA]-[9th-June-2026]-[Fire Service]-[Preventive Maintenance]-Monthly PPM Test Emergency Lighting&Emergency Escape Indicating System | In Progress | 2026-06-09 | 2026-06-04 |  |  |  | CR | CHG0036011 |  | Active | GYA | 2026-06-01 | https://aipostation.apzones.com/change_request.do?sys_id=3ca21689975dc3d064f17606c853afb7&sysparm_record_target=change_request&sysparm_record_row=11&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id
[R3] -[Jun-03-2026]-[ULA] -[Mechanical] - [Preventive Maintenance] -MAU/AHU-Semi Annual PPM& Annual PPM | In Progress | 2026-06-03 | 2026-06-02 |  |  |  | CR | CHG0035993 |  | Active | ULA | 2026-06-01 | https://aipostation.apzones.com/change_request.do?sys_id=3f23839c975dcf9064f17606c853af5c&sysparm_record_target=change_request&sysparm_record_row=12&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id
[R3]-[June-2-2026]-[ULA]-[Electrical]-[Other]- Re-lay the temperature sensors inside battery cabinets | In Progress | 2026-06-02 | 2026-05-28 |  |  |  | CR | CHG0035959 |  | Active | ULA | 2026-05-25 | https://aipostation.apzones.com/change_request.do?sys_id=4496e9769701c7907d637606c853afea&sysparm_record_target=change_request&sysparm_record_row=13&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id
[R2] -[May-12-2026]-[ULA] - [Fire Service]- [Preventive Maintenance] - Fire single point test of Zone Q/R | New | 2026-05-12 | 2026-05-05 |  |  |  | CR | CHG0035858 |  | Active | ULA | 2026-05-04 | https://aipostation.apzones.com/change_request.do?sys_id=46815ceb97ec03d064f1f7cfd853affb&sysparm_record_target=change_request&sysparm_record_row=14&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Status updated from In Progress to New
[R3]-[June-04-2026]-[ULA]-[Fire]-[improvement]GGBM25 #3.8 9602 Replacement of Water Tank Supply Pipeline and Construction of Water Pump Foundation | In Progress | 2026-06-04 | 2026-05-20 |  |  |  | CR | CHG0035939 |  | Active | ULA | 2026-05-18 | https://aipostation.apzones.com/change_request.do?sys_id=4febe5d497c1875064f17606c853af89&sysparm_record_target=change_request&sysparm_record_row=15&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id
[R2]-[GYA]-[11th-June-2026]-[Fire Service]-[Improvement]-The physical construction of GGBM25-3.1 in A+B fire zones | In Progress | 2026-06-11 | 2026-06-04 |  |  |  | CR | CHG0036012 |  | Active | GYA | 2026-06-01 | https://aipostation.apzones.com/change_request.do?sys_id=5cdee28597dd83d07d637606c853af45&sysparm_record_target=change_request&sysparm_record_row=17&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id
[R3] -[06/13/2026]-[GYA] -[Mechanical] - [Preventive Maintenance] -domestic water tank cleaning | Closed | 2026-06-13 09:00:00 | 2026-06-04 11:53:47 |  |  | 2026-06-18 18:00:00 | CR | CHG0036008 |  | Completed | GYA | 2026-06-01 | https://aipostation.apzones.com/change_request.do?sys_id=5e197d4d97d583d07d637606c853af26&sysparm_record_target=change_request&sysparm_record_row=12&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Status updated from In Progress to Closed, URL updated
[R3]-GYA -[Jun-3rd-2026]-[Electrical] -[Preventive Maintenance] -stage 5-Perform diesel generator&SCR sets quarterly&annually PPM. | In Progress | 2026-06-03 | 2026-05-27 |  |  |  | CR | CHG0035955 |  | Active | GYA | 2026-05-25 | https://aipostation.apzones.com/change_request.do?sys_id=5ec52866978947907d637606c853afcb&sysparm_record_target=change_request&sysparm_record_row=19&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id
[R1]-[June-15-2026]-[ULA]-[Electrical]-[GGBM25]- #4.2 Install power meter(0349.LVS01M05-6) & All power meters tie-in to EPMS | In Progress | 2026-06-15 | 2026-06-03 |  |  |  | CR | CHG0036001 |  | Active | ULA | 2026-06-01 | https://aipostation.apzones.com/change_request.do?sys_id=6696487c979d43d064f17606c853afb4&sysparm_record_target=change_request&sysparm_record_row=20&sysparm_record_rows=53&sysparm_record_list=active%3Dtrue%5Eassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5EORassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORDERBYDESCwork_end%5EORDERBYsys_id
【事件概述】：BMS报0453.ACH04故障代码28（油压差高）_x000D_ 【CMMS号】：79208_x000D_ 【发生时间】：2026年6月2日 10:54_x000D_ 【事件来源】：BMS_x000D_ 【事件级别】：Singnificant_x000D_ 【涉及业务】：DH5000及5000区域设备间_x000D_ 【业务影响】：无_x000D_ 【系统状态】：BMS系统自动启动0453.ACH01，冷机出水温度正常_x000D_ 【处置措施】：_x000D_ 10:54 技术员已赶往现场_x000D_ 11:02 0453.ACH01已自动启动_x000D_ 11:03 已通知工程师、运维经理及CFM_x000D_ 11:05 已通知JCI厂家赶往现场查看_x000D_ 11:06 BMS查看运行冷机为0453.ACH01，0453.ACH03；待运行冷机为0453.ACH03，0453.ACH04已故障停机，冷冻水供水正常 | Completed |  | 2026-06-02 11:27:38 |  |  | 2026-06-02 | Slack | Slack001 |  | Completed |  | 2026-06-01 | https://apple.slack.com/archives/C05JC4Q6D8X/p1780370858645149
拆开压缩机油滤发现很多铁屑，JCI目前建议停用此台压缩机，工厂正在评估维修方案 | Completed |  | 2026-06-02 17:32:20 |  |  | 2026-06-02 | Slack | Slack002 |  | Completed |  | 2026-06-01 | https://apple.slack.com/archives/C05JC4Q6D8X/p1780392740108899
&gt; 针对乌兰察布数据中心柴发消音器安装天花板及孔隙封堵事项，现采购部拟定以下方案_x000D_ &gt; 1、乌兰察布数据中心的柴发机组消音器上方没有安装天花板， 导致冬季冷风通过未封堵的位置进入到柴发机组的上方，造成柴发楼内部的水管被冻住/冻裂等情况发生。为避免此类情况的再次发生，本次需要对32台柴发 机组消音器的上方加装天花板，并对目前遗留的孔隙进行封堵； _x000D_ &gt; 2、本次提请的采购服务，在需求的工作说明书中已明确了柴发楼顶棚的现状和安装天花板后的最终成果，使用材料和验收标准。但对于实施过程中完善的服务方案、材料验收、人员登高、实施计划、工器具准备及安排、安全措施等环节均需要专业的服务团队来提供。为了实现期最终天花板安装完毕及所有孔隙封堵的工作，需要选择综合实施方案和商务报价最优、最专业的供应商来实现。所以，本次推荐采用竞争性谈判的方式进行。本次推荐评委人员（技术：孙奎、邹宇、王志宇，商务：李朋、蔡文波），综合评审表见附件起草的文件。 _x000D_ &gt; 3、针对本次服务事项，结合目前乌兰察布数据中心周边有专业施工能力且愿意参与我司项目的供应商资源，经过前期与技术部门共同审核，推荐“天津汇能建筑工程有限公司、陕西百川嘉盈建筑工程有限公司、北京华建嘉瑞工程建设有限公司、维谛技术有限公司“四家供应商参与，本次潜在供应商资源均是具备工程维修改造相关资质、都是经过技术部门审核的。 _x000D_ | Completed |  | 2026-06-04 13:44:39 |  |  | 2026-06-04 | Slack | Slack006 |  | Completed |  | 2026-06-01 | https://apple.slack.com/archives/C05JC4Q6D8X/p1780551879406209
&gt; 针对乌兰察布数据中心“园区内道路标识增加防滑功能“服务事项，现将采购方案拟定如下：_x000D_ &gt; 1、本次提请的是乌兰察布EHS团队识别出来的，目前园区内道路标识无防滑功能，在雨雪天人员行走存在摔伤的风险。在工作说明书中已明确了具体工作量、技术要求，需求内容已明确。_x000D_ &gt; 2、本次采购需求是数据中心EHS管理服务需求的内容，但对现有道路标识整改的具体实施方案、材料选择、进度计划、安全措施等细节部分都需要供应商进行勘查现场后提供综合方案，便于我司综合评估和优先选择最佳实施方案和商务报价的供应商，因此推荐采用竞争性谈判的方式进行。目前推荐评标委员5人（技术：孙奎、杨珂、邹宇，商务：李朋、蔡文波 ），集中评审打分表（商务30分，技术70分）详见附件。 _x000D_ &gt; 3、针对本次“园区内道路标识线防滑整改服务“事项，推荐目前在乌兰察布数据中心周边有维修改造服务支持资源，且经过我司资质预审合格的供应商：“天津汇能建筑工程有限公司、陕西百川嘉盈建筑工程有限公司、北京华建嘉瑞工程建设有限公司、维谛技术有限公司“四家供应商参与，本次潜在供应商资源均是具备工程维修改造相关资质、都是经过技术部门审核的。 _x000D_ | Completed |  | 2026-06-04 13:46:09 |  |  | 2026-06-04 | Slack | Slack008 |  | Completed |  | 2026-06-01 | https://apple.slack.com/archives/C05JC4Q6D8X/p1780551969547819
<@WM2PZHL15> <@W015CNM3P88> please take note that GYA water quality report of May have been uploaded into below box folder, FYI, thx. <https://apple.box.com/s/zf7h201gp5iv8i225y8ix5r7ypi25iee> | Completed |  | 2026-06-04 14:51:03 |  |  | 2026-06-04 | Slack | Slack010 |  | Completed |  | 2026-06-01 | https://apple.slack.com/archives/C05JC4Q6D8X/p1780555863995849
【事件概述】：XA.ULA.<tel:01.01.6000.02.016¦01.01.6000.02.016> Power Strip的B相指示灯熄灭_x000D_ 【CMMS号】：79428_x000D_ 【发生时间】：2026年6月8日 11:37_x000D_ 【事件来源】：IT同事现场发现_x000D_ 【事件级别】： P2_x000D_ 【业务影响】： XA.ULA.01.01.6000.02.016.1 机柜内设备失冗余_x000D_ 【处置措施】： 组织技术员现场进行排查_x000D_ 11:42 测量机柜内Power Strip B相电压为0_x000D_ 11:44 对应6000.02.TAP08.1的2号口 L2保险熔断_x000D_ 11:49 已更换保险，电压恢复正常238.4V，此次应急响应结束 | Completed |  | 2026-06-08 11:58:01 |  |  | 2026-06-08 | Slack | Slack011 |  | Completed |  | 2026-06-08 | https://apple.slack.com/archives/C05JC4Q6D8X/p1780891081853489
[R3]-[GYA] -[Jun-29th-2026]-[Electrical] -[Improvement] -Diesel generator air inlet silencer cleaning | New | 2026-06-29 09:30:00 | 2026-06-23 09:20:34 |  |  | 2026-07-10 21:00:00 | CR | CHG0036094 |  | Active | GYA | 2026-06-22 | https://aipostation.apzones.com/change_request.do?sys_id=033c474b97a1cf507d637606c853af94&sysparm_record_target=change_request&sysparm_record_row=1&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3]-[GYA] -[Jun-25th-2026]-[Civil] -[Improvement] -Repair of Physical security door coordinator&door closer&door latch | Authorize | 2026-06-25 09:00:00 | 2026-06-22 13:40:34 |  |  | 2026-07-08 18:00:00 | CR | CHG0036088 |  | Active | GYA | 2026-06-22 | https://aipostation.apzones.com/change_request.do?sys_id=0e2e3afe97ed4f507d637606c853af94&sysparm_record_target=change_request&sysparm_record_row=5&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3]-[06/24/2026]-[GYA]-[Preventive Maintenance] -Bi-weekly Elevator Maintenance | Authorize | 2026-06-24 09:00:00 | 2026-06-16 13:36:07 |  |  | 2026-06-26 18:00:00 | CR | CHG0036065 |  | Active | GYA | 2026-06-15 | https://aipostation.apzones.com/change_request.do?sys_id=0e9300899761c75064f17606c853afb9&sysparm_record_target=change_request&sysparm_record_row=6&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R1]-[Jul-07-2026]-[ULA]-[Fire]-[Retrofit]GGBM25 #3.1 Rectification of fire-fighting cables of fire zone B (DH2000) | Authorize | 2026-07-07 09:00:00 | 2026-06-22 09:31:35 |  |  | 2026-07-20 23:00:00 | CR | CHG0036092 |  | Active | ULA | 2026-06-22 | https://aipostation.apzones.com/change_request.do?sys_id=0f258ab297e94f507d637606c853aff0&sysparm_record_target=change_request&sysparm_record_row=7&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R2]-[Jun-13-2026]-[ULA]-[Mechanical]-[Corrective Maintenance] - Replacement of the 0447.ACH03 system1 compressor | Implement | 2026-06-13 10:00:00 | 2026-06-12 15:39:53 |  |  | 2026-06-26 22:00:56 | CR | CHG0036050 |  | Active | ULA | 2026-06-08 | https://aipostation.apzones.com/change_request.do?sys_id=1099f76f97518b107d637606c853afea&sysparm_record_target=change_request&sysparm_record_row=8&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3] -[June-15-2026]-[ULA] -[Mechanical] - [Corrective Maintenance] -Replacement of fuel filter oil pipes and valves for 0461/0462 | Implement | 2026-06-15 09:00:00 | 2026-06-10 10:19:57 |  |  | 2026-06-26 18:00:00 | CR | CHG0036034 |  | Active | ULA | 2026-06-08 | https://aipostation.apzones.com/change_request.do?sys_id=162dd0c3979587107d637606c853af5b&sysparm_record_target=change_request&sysparm_record_row=10&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3]-[Jun-25th-2026]-[GYA]-[Electrical]-[Preventive Maintenance]-LV cabinet filter replacement and thermal imaging& transformer thermal imaging annually | Authorize | 2026-06-25 09:30:00 | 2026-06-18 10:23:43 |  |  | 2026-07-08 18:00:00 | CR | CHG0036078 |  | Active | GYA | 2026-06-15 | https://aipostation.apzones.com/change_request.do?sys_id=17bae5a1972d8b5064f17606c853afbc&sysparm_record_target=change_request&sysparm_record_row=11&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R2] -[June-23-2026 ] -[ULA] -[Fire Service]-[Preventive Maintenance]-Fire door and fire shutter door monthly PPM | Implement | 2026-06-23 09:00:00 | 2026-06-16 17:34:22 |  |  | 2026-06-25 23:00:00 | CR | CHG0036067 |  | Active | ULA | 2026-06-15 | https://aipostation.apzones.com/change_request.do?sys_id=182ab0819729c75064f17606c853afb0&sysparm_record_target=change_request&sysparm_record_row=12&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R1]-[GYA]-[30th-June-2026]-[Fire Service]-[Improvement]-The rectification of fire cable issues and L3 test in M+P fire zones(CR Extension) | Authorize | 2026-06-30 10:00:00 | 2026-06-17 16:33:59 |  |  | 2026-07-14 10:00:00 | CR | CHG0036071 |  | Active | GYA | 2026-06-15 | https://aipostation.apzones.com/change_request.do?sys_id=25e57555976d87507d637606c853af98&sysparm_record_target=change_request&sysparm_record_row=17&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R2] -[June-22-2026]-[ULA] - [Fire Service]- [Preventive Maintenance] - Emergency lighting and evacuation system PPM - Monthly | Implement | 2026-06-22 09:00:00 | 2026-06-16 22:48:17 |  |  | 2026-06-24 23:00:00 | CR | CHG0036069 |  | Active | ULA | 2026-06-15 | https://aipostation.apzones.com/change_request.do?sys_id=26f1424d972dc75064f17606c853af1f&sysparm_record_target=change_request&sysparm_record_row=19&sysparm_record_rows=90&sysparm_record_list=active%3Dtrue%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R2] -[June-17-2026] -[ULA] -[Fire Service]- [Preventive Maintenance] -Water mist system monthly PPM | Closed | 2026-06-17 09:00:00 | 2026-05-07 10:31:49 |  |  | 2026-06-23 23:00:00 | CR | CHG0035868 |  | Completed | ULA | 2026-05-04 | https://aipostation.apzones.com/change_request.do?sys_id=fcd91944973c83d064f17ac8d853af49&sysparm_record_target=change_request&sysparm_record_row=1&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R1]-[Jun-09-2026]-[ULA]-[Fire]-[Retrofit]GGBM25 #3.1 Rectification of fire-fighting cables of fire zone B (DH2000) | Closed | 2026-06-09 09:00:00 | 2026-05-14 17:46:37 |  |  | 2026-06-22 23:00:00 | CR | CHG0035905 |  | Completed | ULA | 2026-05-11 | https://aipostation.apzones.com/change_request.do?sys_id=b970cf5297f00f1064f17606c853af07&sysparm_record_target=change_request&sysparm_record_row=2&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3] -[June-22-2026]-[ULA] -[Mechanical] - [Preventive Maintenance] -Elevator 2W Maintenance | Closed | 2026-06-22 09:00:00 | 2026-06-16 13:38:01 |  |  | 2026-06-23 18:00:00 | CR | CHG0036063 |  | Completed | ULA | 2026-06-15 | https://aipostation.apzones.com/change_request.do?sys_id=b5044ccd9761c75064f17606c853af68&sysparm_record_target=change_request&sysparm_record_row=3&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3]-[06/18/2026]-[GYA]-[Corrective Maintenance] -9326.EF01 repairing | Closed | 2026-06-18 09:00:00 | 2026-06-16 09:00:00 |  |  | 2026-06-26 18:00:00 | CR | CHG0036062 |  | Completed | GYA | 2026-06-15 | https://aipostation.apzones.com/change_request.do?sys_id=6d648f7c97e9875064f17606c853af08&sysparm_record_target=change_request&sysparm_record_row=4&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3] -[Jun-15-2026]-[ULA]-[BMS]-[Preventive Maintenance]- BMS two Monthly Preventive Maintenance | Closed | 2026-06-15 08:50:00 | 2026-06-10 10:54:51 |  |  | 2026-06-26 22:00:00 | CR | CHG0036036 |  | Completed | ULA | 2026-06-08 | https://aipostation.apzones.com/change_request.do?sys_id=d5252c07971d8b1064f17606c853af62&sysparm_record_target=change_request&sysparm_record_row=6&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R2]-[8th-Jun-2026]-[GYA]-[CFM]-[Electrical]-[Preventive Maintenance] - stage 2-Phase I&II&III UPS Annual PPM | Closed | 2026-06-08 09:00:00 | 2026-05-15 13:51:18 |  |  | 2026-06-21 18:00:00 | CR | CHG0035916 |  | Completed | GYA | 2026-05-11 | https://aipostation.apzones.com/change_request.do?sys_id=b0341b2e97f04f107d637606c853af00&sysparm_record_target=change_request&sysparm_record_row=9&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3] -[June-17-2024] -[ULA] -[Fire Service] - [Corrective Maintenance] -Replacement of the faulty ASD detector motherboard | Closed | 2026-06-17 09:00:00 | 2026-06-15 10:07:39 |  |  | 2026-06-25 23:00:00 | CR | CHG0036057 |  | Completed | ULA | 2026-06-15 | https://aipostation.apzones.com/change_request.do?sys_id=ea4a82a497a9075064f17606c853afe5&sysparm_record_target=change_request&sysparm_record_row=10&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3] -[June-17-2024] -[ULA] -[Fire Service] - [Corrective Maintenance] -Replacement of Power Amplifier for Fire Emergency Broadcast 6# | Closed | 2026-06-17 09:00:00 | 2026-06-15 09:16:29 |  |  | 2026-06-18 23:00:00 | CR | CHG0036055 |  | Completed | ULA | 2026-06-15 | https://aipostation.apzones.com/change_request.do?sys_id=c19e31e09769075064f17606c853af40&sysparm_record_target=change_request&sysparm_record_row=11&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3]-[GYA]-[06/09/2026]-[BMS]-[improvement]-VAV alarm optimization | Closed | 2026-06-09 09:30:00 | 2026-06-03 10:22:23 |  |  | 2026-06-18 18:00:00 | CR | CHG0036000 |  | Completed | GYA | 2026-06-01 | https://aipostation.apzones.com/change_request.do?sys_id=e99a90b0975503d07d637606c853af8c&sysparm_record_target=change_request&sysparm_record_row=13&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3]-[6/15/2026]-[GYA]-[EPMS]-[Preventive maintenance]-Quarterly EPMS maintenance | Closed | 2026-06-15 09:30:00 | 2026-06-02 09:13:42 |  |  | 2026-06-18 20:00:00 | CR | CHG0035992 |  | Completed | GYA | 2026-06-01 | https://aipostation.apzones.com/change_request.do?sys_id=e141cb14975dcf9064f17606c853aff6&sysparm_record_target=change_request&sysparm_record_row=14&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3]-[June-17-2026]-[ULA]-[Electrical]-[Preventive Maintenance]- Charging Pile Quarterly PM | Closed | 2026-06-17 09:00:00 | 2026-06-11 14:07:21 |  |  | 2026-06-24 21:00:00 | CR | CHG0036047 |  | Completed | ULA | 2026-06-08 | https://aipostation.apzones.com/change_request.do?sys_id=83ca565b97510b107d637606c853afaa&sysparm_record_target=change_request&sysparm_record_row=15&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3]-[GYA]-[16th-June-2026]-[Fire Service]-[Maintenance]-Replace the batteries of ASD/FEP/EPS | Closed | 2026-06-16 10:00:00 | 2026-06-12 13:56:35 |  |  | 2026-06-17 20:00:00 | CR | CHG0036049 |  | Completed | GYA | 2026-06-08 | https://aipostation.apzones.com/change_request.do?sys_id=1be16f2f97dd4b107d637606c853afd7&sysparm_record_target=change_request&sysparm_record_row=16&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R2] -[June-15-2026]-[ULA] - [Fire Service]- [Preventive Maintenance] -Maintenance of ASD for Fire Protection Systems -Zone E&G（North Network area） | Closed | 2026-06-15 09:00:00 | 2026-06-10 13:59:07 |  |  | 2026-06-18 23:00:00 | CR | CHG0036040 |  | Completed | ULA | 2026-06-08 | https://aipostation.apzones.com/change_request.do?sys_id=fc5fcd0f9751cb1064f17606c853af7c&sysparm_record_target=change_request&sysparm_record_row=17&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R2] -[June-15-2026]-[ULA] - [Fire Service]- [Preventive Maintenance] -Fire power supply monitoring, electrical fire, fireproof doors system-PPM-Zone E&G -A | Closed | 2026-06-15 09:00:00 | 2026-06-11 13:33:06 |  |  | 2026-06-18 23:00:00 | CR | CHG0036046 |  | Completed | ULA | 2026-06-08 | https://aipostation.apzones.com/change_request.do?sys_id=91f29a9f971d4f1064f17606c853af6c&sysparm_record_target=change_request&sysparm_record_row=18&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3]-[06/03/2026]-[GYA]-[Mechanical]-[Preventive Maintenance]-ACH- Semi-annual maintenance+annual maintenance-Part4 | Closed | 2026-06-03 09:00:00 | 2026-04-16 11:27:10 |  |  | 2026-06-16 18:00:00 | CR | CHG0035799 |  | Completed | GYA | 2026-04-13 | https://aipostation.apzones.com/change_request.do?sys_id=e21d99dd9718875013407ac8d853af51&sysparm_record_target=change_request&sysparm_record_row=19&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL
[R3]-[Jun-12-2026]-[ULA]-[Mechanical]-[Preventive Maintenance ] -Urea Water-Q PPM | Closed | 2026-06-12 09:30:00 | 2026-06-11 09:00:37 |  |  | 2026-06-17 22:01:37 | CR | CHG0036042 |  | Completed | ULA | 2026-06-08 | https://aipostation.apzones.com/change_request.do?sys_id=06941dd397d9c7107d637606c853afdb&sysparm_record_target=change_request&sysparm_record_row=20&sysparm_record_rows=2837&sysparm_record_list=active%3Dfalse%5Eassignment_group%3Db73b3701ad1a501064f15f8a6780a95e%5EORassignment_group%3Dfc1bb301ad1a501064f15f8a6780a972%5Ework_endISNOTEMPTY%5EORDERBYDESCwork_end%5EORDERBYsys_id | [2026-06-23] Appended new row with URL

## Concerns&Comments
Week_Start (Exact Date) | Highlight_ID | Impact_Level (High/Medium/Low) | Title
46020 | 2026W01_01 | Low | Weekly closure throughput improved
46020 | 2026W01_02 | Medium | Backlog pressure observed in selected queue
46027 | 2026W02_01 | Low | Weekly closure throughput improved
46027 | 2026W02_02 | Medium | Backlog pressure observed in selected queue
46034 | 2026W03_01 | Low | Weekly closure throughput improved
46034 | 2026W03_02 | Medium | Backlog pressure observed in selected queue
46041 | 2026W04_01 | Low | Weekly closure throughput improved
46041 | 2026W04_02 | Medium | Backlog pressure observed in selected queue
46048 | 2026W05_01 | Low | Weekly closure throughput improved
46048 | 2026W05_02 | Medium | Backlog pressure observed in selected queue
46055 | 2026W06_01 | Low | Weekly closure throughput improved
46055 | 2026W06_02 | Medium | Backlog pressure observed in selected queue
46062 | 2026W07_01 | Low | Weekly closure throughput improved
46062 | 2026W07_02 | Medium | Backlog pressure observed in selected queue
46069 | 2026W08_01 | Low | Weekly closure throughput improved
46069 | 2026W08_02 | Medium | Backlog pressure observed in selected queue
46076 | 2026W09_01 | Low | ULA Incident
46076 | 2026W09_02 | Medium | GYA Incident
46083 | 2026W10_01 | High | ULA HSE Room Total Cooling Loss Incident
46083 | 2026W10_02 | High | GYA PAV quick exhaust valve issue
46090 | 2026W11_01 | Medium | Purified Water Dosing Procedure for Urea Solution
46090 | 2026W11_02 | Medium | GEN24, GEN12#柴发不在自动位报警的调查
46090 | 2026W11_03 | Medium | BM27 Items Discussisng
46097 | 2026W12_01 | Low | ULA Municipal Water Supply Low Pressure
46097 | 2026W12_02 | Low | GYA air duct bracket issue
46104 | 2026W12_01 | Medium | [GYA]-Significant Incident Summary -0443.ACH03 sys2 fan fault alarm
46104 | 2026W12_02 | Low | ULA Combustable Gas Detector Repair or Refresh Discussion
46104 | 2026W12_03 | Low | Syncing up for the feedback from AIPO about the FY26 BM list
46111 | 2026W13_01 | Medium | ULA P2 Incident- The connector of pressure stabilizing pump in water mist system in 5601 leakage.
46111 | 2026W13_02 | Medium | ULA Data Building Domestic Water Pipes Do Not Form a Closed Ring
46118 | 2026W14_01 | High | [GYA]-Significant Incident Summary -0447.ACH02 sys2 high motor temperature alarm
46118 | 2026W14_02 | Medium | [ULA]-The low-voltage switchgear in Room 5304 is vibrating and making a loud noise.
46118 | 2026W14_03 | Low | BM26 Eye wash station Scop Discussion
46118 | 2026W14_04 | Low | Engineering Exploration- HPWM Isolation Valve Discussion & Decision
46125 | 2026W15_01 | Medium | ULA - 4601 HPWM compressed air pipe leak
46125 | 2026W15_02 | Medium | ULA- 0447-3# Cold Machine System 2 fault, Code 33 (Oil separator ejector fault)
46125 | 2026W15_03 | Low | Marriof presssure onsite test. (HPWM)
46125 | 2026W15_04 | Low | BM26 item scope clarification.
46132 | 2026W16_01 | High | GYA- incident-[P1]-captured the smoke alarm message in the corridor of 0130 area
46132 | 2026W16_02 | Medium | Incident Follow up - ULA -The Water MeterShows an Abnormally High Water Consumption
46132 | 2026W16_03 | Low | 岩棉问题（ULA+GYA）的讨论
46132 | 2026W16_04 | Low | BM Item: 氮气发生装置的讨论；
46139 | 2026W17_01 | High | Deep dive - incident-[P1]-captured the smoke alarm message in the corridor of 0130 area
46146 | 2026W18_01 | High | RCA Analysis & Team discussion- incident-[P1]-captured the smoke alarm message in the corridor of 0130 area
46146 | 2026W18_02 | Medium | ULA: EPMS 出现大量告警 (No Bussiness impact)
46153 | 2026W19_01 | Medium | Follow up- incident-[P1]-captured the smoke alarm message in the corridor of 0130 area
46153 | 2026W19_02 | Medium | ULA: 冷机返厂维修
46153 | 2026W19_03 | Medium | Team Disscusion: 燃油系统系统供应商和RFP process.
46160 | 2026W20_01 | Medium | Follow up- incident-[P1]-captured the smoke alarm message in the corridor of 0130 area.
46160 | 2026W20_02 | Medium | CBRE service renew and commercial confirmtion.
46160 | 2026W20_03 | Medium | ULA 红线外电线杠施工关注.
46167 | 2026W21_01 | Medium | Follow up- incident-[P1]-captured the smoke alarm message in the corridor of 0130 area (BIg group review)
46167 | 2026W21_02 | Low | Team review for small enhancement on May.
46174 | 2026W22_01 | Medium | DCO Confirmation- incident-[P1]-captured the smoke alarm message in the corridor of 0130 area.
46174 | 2026W22_02 | Medium | Team disscusion: JCI RCA follow up action.
46181 | 2026W23_01 | High | Team discussion: ULA DH4000 3#冷机（0447.ACH03）系统1压缩机 - 返厂维修.
46181 | 2026W23_02 | Medium | DCO Confirmation: incident-[P1]-captured the smoke alarm message in the corridor of 0130 area.
46181 | 2026W23_03 | Low | Incident Follow up: XA.ULA.01.01.6000.02.016 Power Strip的B相指示灯熄灭.

## DC Industry
Week Start | Category | Title | Summary | Source | Region | URL | Published Date
46181 | Policy & Regulation | MIIT releases 2026 green data center evaluation framework | Updated guidance sets tiered PUE targets by climate zone, mandates renewable energy mix reporting, and introduces annual compliance audits for facilities above 5MW IT load. | MIIT | China | https://www.miit.gov.cn/ | 46181
46181 | Policy & Regulation | Inner Mongolia energy bureau requires monthly diesel generator runtime logs | All hyperscale and colocation operators in key industrial parks must submit backup generator utilization data; non-compliance may affect expansion permits. | Inner Mongolia Energy Bureau | China | https://nyj.nmg.gov.cn/ | 46181
46181 | Policy & Regulation | EU Energy Efficiency Directive reporting window opens for Q2 | Operators with EU footprint must disclose facility-level energy performance metrics; liquid cooling deployments may qualify for revised accounting methods. | European Commission | EU | https://energy.ec.europa.eu/topics/energy-efficiency/energy-efficiency-directive_en | 46181
46181 | Market & Industry | North China wholesale colocation absorption remains strong | Major providers report 85%+ pre-leasing on new phases; AI training clusters continue to drive demand for 40–60kW racks and dedicated liquid-cooling zones. | Synergy Research | China | https://www.synergyresearchgroup.com/data-center-research/ | 46181
46181 | Market & Industry | Hyperscalers accelerate secondary market expansion beyond Tier-1 cities | ULA and surrounding regions see increased land banking activity as cloud and AI operators seek lower power costs and renewable energy access. | IDC Marketscape | China | https://www.idc.com/research/data-center.jsp | 46181
46181 | Market & Industry | GYA corridor attracts new fiber backbone investments | Two carriers announce redundant long-haul routes to support rising east-west traffic between Beijing metro and western compute hubs. | Light Reading | China | https://www.lightreading.com/cable-technology | 46181
46181 | Standards & Compliance | NFPA 75 update clarifies lithium battery room monitoring requirements | Revised checklist adds continuous thermal imaging options and emergency ventilation verification for rooms above 600kWh installed capacity. | NFPA | Global | https://www.nfpa.org/codes-and-standards/all-codes-and-standards/list-of-codes-and-standards/detail?code=75 | 46181
46181 | Standards & Compliance | GB 50174 data center design standard alignment review underway | Working group proposes tighter hot-aisle containment requirements and updated fire compartmentation guidance for high-density halls. | MOHURD / GB Standards | China | https://openstd.samr.gov.cn/bzgk/gb/index | 46181
46181 | Standards & Compliance | ISO 50001 surveillance audits emphasize M&V for cooling plants | Certification bodies request additional evidence of chiller plant efficiency tracking and corrective action logs for sites above 10MW cooling load. | ISO / BSI | Global | https://www.iso.org/standard/69425.html | 46181
46181 | Technology & Innovation | Liquid-to-chip cooling reference designs gain traction for 50kW+ racks | Vendors publish CDU integration guides for existing chilled-water plants; early adopters report 8–12% reduction in facility PUE at high AI utilization. | ASHRAE TC 9.9 | Global | https://tc0909.ashraetcs.org/ | 46181
46181 | Technology & Innovation | HVDC distribution pilots show promise for AI cluster power delivery | 800V DC bus architectures reduce copper losses in last-mile power distribution; several operators evaluating staged rollout in new builds only. | OCP Global Summit | Global | https://www.opencompute.org/projects/advanced-cooling-solutions | 46181
46181 | Technology & Innovation | DCIM platforms add AI workload-aware capacity forecasting | New modules correlate GPU utilization patterns with cooling and power headroom, enabling week-ahead capacity planning for training bursts. | Uptime Intelligence | Global | https://uptimeinstitute.com/resources/research-and-reports | 46181
46181 | Technology & Innovation | Battery energy storage systems paired with on-site renewables expand in northern China | Hybrid solar + BESS deployments help operators smooth grid peaks and improve renewable utilization scores under new green DC scoring rules. | BNEF | China | https://about.bnef.com/blog/ | 46181